## Sheet1
DCS6 Programming Guide
|  |  |  | Model # |  | DCS6-210-150-T2
Serial #
|  |  |  | Software Rev |  | 520.7
Configuration Settings (Press and Hold)
press and hold for 5 sec. Next & release and press and hold for 5 sec. Next &
Set Valve Type (1.0, 1.0t 1.25, 1.5, 2.0)
1.5
Flow Meter Size (FL 1.5, 2.0, 3.0, 1.0r, PUL)
FL 1.5
Set DP (OFF, on0, dEL, HoLd )
OFF
Set (NHWBP, ALT A, ALT b, SEPS, SYS or OFF)
ALT A/B
When ALT is Selected see below note.
1.0", 1.25"& 1.5" (dELAY or off) for rinse/fill |  |  |  | 2"or 1.0t set pre rinse time or off
| N/A |  |  |  | N/A
Fill Units (For 1.5") MIN or LBS
MIN
Set Regen Cycle Times (Press and Hold)
press and hold for 5 sec Next &
Set ( Softening / Filtering)
Softening
Brining Direction (dn or up)
dn
Refil Location (PoST or PrE)
PoST
Backwash time
10
Brine time
60
Second Backwash time
OFF
Rinse time
10
Fill Setting for ( 1.0, 1.0t, 1.25 will be in LBS/ for 1.5" LBS or min, 2" min.)
46.5 @10#
Set System Capacity
174
Set Volume Capacity (AUTO or oFF)
AUTO
Set Regeneration Time Options (on0, Normal, on0 + normal)
on 0
Set Relay Operation (Time on, Gallons Softening on, Gallons softening regen, Error, oFF)
OFF
Set Relay Actuation Time or Gallons
N/A
Set Rely Deactivation Time
N/A
Installer Display Settings (Press and Hold)
Next &
Hardness
Set Day Override
OFF
Set Regen Time
on 0
Date
Programming Completed By: